## Electricity Consumption
National Health Laboratory Services (EC Region)
Manual Total Load Sizing Chart
Nelson Mandela Bay & Sarah Baartman (NMBSB)
Humansdorp Laboratory
Item | Appliance/Analyzer/Machine | Type | Load (WATTS) Running | Load (WATTS) Starting | Quantity | Total
1 | Air Conditioner | 10000 BTU | 2000 | 5000 | 3 | 6000
|  | 20000 BTU | 3000 | 7500 |  | 0
|  | 24000 BTU | 4500 | 11250 |  | 0
2 | Water Pump | Large | 2000 | 5000 | 1 | 2000
3 | Geyser | 150l | 2000 |  | 1 | 2000
4 | AU480 | 3.5 kVA | 3500 | 3500 | 1 | 3500
5 | Sysmex XN530 |  | 640 |  | 1 | 640
6 | cobas h232 | small | 6.8 |  | 1 | 6.8
7 | BFTII | small | 264 |  | 1 | 264
8 | heating box |  | 100 |  | 1 | 100
9 | Roller mixer |  | 110 |  | 1 | 110
10 | Microscope |  | 110 |  | 1 | 110
Hi-Tech/Audio Visual
1 | Desktop Computer |  | 300-600 |  | 4 | 1600
2 | Laptop |  | 70-150 |  | 1 | 150
3 | UPS/Inverter |  | 100-600 |  | 4 | 1600
4 | Printer |  | 60-1500 |  | 5 | 2750
5 | Cellphone Charger |  | 9-20 |  | 2 | 40
6 | Telephone |  | 60-100 |  | 2 | 200
7 | Access Control |  | 300-600 |  | 1 | 600
8 | LCD/LED Screen |  | 80-130 |  | 2 | 260
9 | Amano date and time |  | 150 |  | 4 | 1000
10 | Thermal labels printers |  | 125 |  | 3 | 375
11 | Server |  | 500-1500 |  | 1 | 1500
Kitchen Appliances
1 | Heater (per bar) |  | 1000-3000 |  | 3 | 2400
2 | Freezer |  | 400-600 |  | 1 | 600
3 | Kettle |  | 850-2000 |  | 1 | 1000
4 | Microwave |  | 1000-3000 |  | 1 | 1500
5 | Fridge |  | 550-2500 |  | 3 | 1500
6 | Toaster |  | 750-1250 |  | 1 | 750
7 | Water Cooler |  | 580 |  | 1 | 580
Lighting/Lights
1 | Domestic Lights (per bulb) |  | 40-100 |  | 21 | 2100
2 | Outside Lights |  | 100-1000 |  | 8 | 2000
3 | Specialized Domestic Lights |  | 100-1000 |  | 5 | 750
4 | Energy Saver Light bulb |  | 10-20 |  | 10 | 200
| (Sub-total/1000kw) |  | 19085.8 | 32250 |  | 38185.8
| (kW/0,8)kVA: |  |  |  |  | 38.1858
| kVA Total: |  |  |  |  | 47.7323