## Sheet1
Business Unit | NMAL
Laboratory | Cytology
Req. # | 1859938
| Comply | Don't Comply
GENERAL
Battery Enclosure Type
Internal
Subcategory
UPS
Manufacturer
Schneider Electric
POWER DEVICE
Voltage Required
AC 100 V
Power Output Connectors Details
8 x power NEMA 5-15
2 x power NEMA 5-20
Output Voltage
AC 100 V ± 5% - 47 - 53 / 57 - 63 Hz
Power Capacity
4.8 kW / 6000 VA
Surge Suppression
yes
Surge Energy Rating
510 Joules
Power Provided
1.98 kW
Frequency Required
50/60 Hz
Circuit Protection
circuit breaker
Form Factor
external
UPS Technology
line interactive
Voltage Provided
AC 100 V
Voltage Provided Margin
± 5%
Frequency Provided
47 - 53 / 57-63 Hz
UPS Output Waveform
sinewave
Power Capacity (VA)
2200 VA
Input Connector Type
power NEMA L5-30
Input Connector Qty
1
Output Connector Qty
10
Surge Response Time
0 ms
Power Device Features
Automatic Voltage Regulation (AVR), LED indicators, audible alarm, automatic self-test, emergency power off, predicitive failure notification
BATTERY
Quantity
1
Run Time (Up To)
6.7 min at full load
Recharge Time
4.5 hour(s)
Load Type
at full load
NETWORKING
Remote Management Interface
RS-232, USB
INTERFACE PROVIDED
Qty
1
Connector Type
9 pin D-Sub (DB-9)
Type
EPO (emergency power off), management (RS-232), management (USB)
MISCELLANEOUS
Color
black
Color Category
black
ENVIRONMENTAL PARAMETERS
Min Operating Temperature
32 °F
Max Operating Temperature
104 °F
Humidity Range Operating
0 - 95%
EXPANSION SLOTS
Type
SmartSlot
Total Qty
1
CABLE DETAILS
Type
power cable
Length
8 ft
DIMENSIONS & WEIGHT
Width
7.7 in
Depth
21.4 in
Height
17 in
Weight
112.66 lbs
DIMENSIONS & WEIGHT (SHIPPING)
Width (Shipping)
15 in
Depth (Shipping)
30 in
Height (Shipping)
22 in
Weight (Shipping)
134.26 lbs
POWER OUTPUT CONNECTORS DETAILS
Connector Type
power NEMA 5-15, power NEMA 5-20
Connector Qty
2, 8
RUN TIME DETAILS
Run Time (Up To)
6.7 min
Load Type
full load
UPS
Batteries Qty
1
Battery Technology
lead acid
SERVICE & SUPPORT
Type
3 years warranty
SERVICE & SUPPORT DETAILS
Type
limited warranty
Full Contract Period
3 years
Lab manager | Jason de Caires
JDC
Signature
Date | 2026-03-25
Authorised by
Signature
Date

## Draft
1. Power Quality & Topology
Double-Conversion Online (Required): This is the "gold standard" for 6kVA units. It ensures zero transfer time between utility and battery power, isolating your equipment from all grid anomalies.
Pure Sine Wave Output: Essential for sensitive IT and medical equipment to prevent hardware damage or system crashes.
Power Factor (PF): Look for a PF of 1.0 (Unity). A 6kVA UPS with a 1.0 PF provides 6kW of real power, whereas an older 0.7 PF model only provides 4.2kW, effectively giving you less usable capacity for the same rating.
2. Battery & Runtime Management
Battery Chemistry:
Lithium-Ion (LiFePO4): Offers a longer lifespan (8–10 years) and lighter weight, reducing maintenance visits but increasing upfront cost.
VRLA (Lead-Acid): Lower initial cost but requires replacement every 3–5 years.
Scalability: Ensure the unit supports External Battery Packs (EBP) if you need to increase backup time from minutes to hours.
Charging Speed: A high-quality 6kVA unit should recharge to 90% capacity within 3–4 hours to be ready for back-to-back outages.
3. "Smart" Monitoring & Connectivity
Environmental Monitoring: Advanced cards can monitor room temperature and humidity, which is critical since high heat can halve battery life.
4. Operational Efficiency & Environment
Efficiency Rating: Prioritize units with ≥94% efficiency in online mode to reduce electricity bills and heat dissipation.
Form Factor: Choose a Rack/Tower Convertible design for flexibility in where it is installed (standard server rack vs. freestanding).
Noise Levels: Ensure the unit is rated below 50–55 dB(A) if it will be placed in an office environment rather than a dedicated server room
5. Maintenance & Support
Bypass Capability: Must include an internal automatic and manual bypass. This allows you to service or replace the UPS without powering down your connected equipment.
Warranty & Service: Demand at least a 2-year warranty that includes the battery. Check for local support providers like JUP Solutions or Schneider Electric who offer on-site maintenance in South Africa.
JUP Solutions +2
Would you like me to help you calculate the exact runtime for your current equipment load to see if 6kVA is the right size?

## Evaluation Criteria
6KVA Smart UPS Specification | Comply | Don't Comply
1. Power Quality & Topology
1.1 Double-Conversion Online:
1.2 Pure Sine Wave Output:
1.3 Power Factor (PF): PF of 1.0 (Unity).
2. Battery & Runtime Management
2.1 Battery Chemistry:
2.2 Lithium-Ion (LiFePO4):
2.3 Scalability: Ensure the unit supports External Battery Packs (EBP).
2.4 Charging Speed: A high-quality 6kVA unit should recharge to 90% capacity within 3–4 hours to be ready for back-to-back outages.
3. "Smart" Monitoring & Connectivity
3.1 Environmental Monitoring:
4. Operational Efficiency & Environment
4.1 Efficiency Rating: Prioritize units with ≥94% efficiency in online mode.
4.2 Form Factor: Tower Convertible design.
4.3 Noise Levels: Rated below 50–55 dB(A).
5. Maintenance & Support
5.1 Bypass Capability: Include an internal automatic and manual bypass.
5.2 Warranty & Service: 3-year warranty that includes the battery.